## Instructions
Gridworks EMBR — Cymcap Validation Matrix
15 kV & 25 kV cable libraries · assignment worksheet
Purpose
EMBR v1.2 added 15 kV and 25 kV cable libraries (Southwire SPEC 81102 / 81142). These voltage classes are not in the existing 35 kV Cymcap matrix and have no CIGRE TB 880 reference case. This workbook is the assignment to cross-check EMBR's 15/25 kV ratings against Cymcap 8.1 Rev 2, mirroring the 35 kV validation approach.
What to do
1. Build each scenario on the 'Cymcap Matrix' tab in Cymcap 8.1 Rev 2 using the input columns exactly as listed.
2. Cable = single-core Al 1350 TR-XLPE, 100% IL, 1/3 concentric neutral, touching trefoil. 15 kV = 175 mil wall; 25 kV = 260 mil.
3. Conductor limit 90 °C. Multi-point (solidly) bonded concentric neutral. 60 Hz.
4. Enter the Cymcap steady-state ampacity in the yellow 'Cymcap rating (A)' column. The Δ% and Pass/Fail columns fill in automatically.
5. Acceptance criterion: EMBR within ±5% of Cymcap (same as the 35 kV matrix).
6. Flag any scenario that fails, and note Cymcap model settings used (bonding, backfill/native split, dry-out) in the Notes column.
Column legend
• Input columns (A–M): scenario definition — enter these into Cymcap. Soil resistivity is in °C·cm/W (EMBR/Cymcap convention); EMBR uses K·m/W internally = value ÷ 100.
• EMBR rating (A): EMBR v1.2 predicted steady-state ampacity (the physical rating, before EMBR's separate 5% design buffer). This is the comparison target.
• Cymcap rating (A) [YELLOW — you fill in]: the Cymcap steady-state ampacity for the identical scenario.
• Δ% and Within ±5%?: computed automatically once the Cymcap value is entered.
• EMBR w/ 5% buffer (A): the value EMBR shows end users (rating × 0.95); shown for reference only — do NOT compare against this.
Example (illustrative — not a real scenario)
If EMBR rating = 330 A and you enter Cymcap = 342 A → Δ% = +3.6% → PASS (within ±5%).
Prepared by EMBR v1.2 · engine verified against CIGRE TB 880 (33 kV) and an independent IEC 60287 recomputation for 15/25 kV.

## Cymcap Matrix
EMBR 15 kV / 25 kV Cymcap Validation Matrix — enter Cymcap results in the yellow column
Scenario ID | Voltage class (kV) | Operating V (kV) | Cable size | Install | # Circuits | Circuit spacing (in) | Burial depth (in) | Soil temp (°C) | Soil ρ native (°C·cm/W) | Dry-out ρ (°C·cm/W) | Dry-out zone | Load factor | EMBR rating (A) | Cymcap rating (A) | Δ% | Within ±5%? | EMBR w/ 5% buffer (A) | Notes
MV15-01 | 15 | 13.8 | 4/0 AWG | Direct | 1 | 48 | 36 | 25 | 90 | 250 | Yes | 1 | 207 |  |  |  | 196.6 | Base: direct-buried trefoil, single circuit
MV15-02 | 15 | 13.8 | 250 kcmil | Direct | 1 | 48 | 36 | 25 | 90 | 250 | Yes | 1 | 227.2 |  |  |  | 215.8 | Base: direct-buried trefoil, single circuit
MV15-03 | 15 | 13.8 | 350 kcmil | Direct | 1 | 48 | 36 | 25 | 90 | 250 | Yes | 1 | 272.6 |  |  |  | 258.9 | Base: direct-buried trefoil, single circuit
MV15-04 | 15 | 13.8 | 500 kcmil | Direct | 1 | 48 | 36 | 25 | 90 | 250 | Yes | 1 | 329.5 |  |  |  | 313 | Base: direct-buried trefoil, single circuit
MV15-05 | 15 | 13.8 | 750 kcmil | Direct | 1 | 48 | 36 | 25 | 90 | 250 | Yes | 1 | 411.6 |  |  |  | 391 | Base: direct-buried trefoil, single circuit
MV15-06 | 15 | 13.8 | 1000 kcmil | Direct | 1 | 48 | 36 | 25 | 90 | 250 | Yes | 1 | 484.7 |  |  |  | 460.4 | Base: direct-buried trefoil, single circuit
MV15-07 | 15 | 13.8 | 4/0 AWG | Conduit | 1 | 48 | 36 | 25 | 90 | 250 | Yes | 1 | 194 |  |  |  | 184.3 | In PVC-40 conduit, single circuit
MV15-08 | 15 | 13.8 | 500 kcmil | Conduit | 1 | 48 | 36 | 25 | 90 | 250 | Yes | 1 | 304.3 |  |  |  | 289 | In PVC-40 conduit, single circuit
MV15-09 | 15 | 13.8 | 1000 kcmil | Conduit | 1 | 48 | 36 | 25 | 90 | 250 | Yes | 1 | 489.5 |  |  |  | 465 | In PVC-40 conduit, single circuit
MV15-10 | 15 | 13.8 | 500 kcmil | Direct | 2 | 18 | 36 | 25 | 90 | 250 | Yes | 1 | 309.9 |  |  |  | 294.4 | Two circuits, 18 in c/c, direct buried
MV15-11 | 15 | 13.8 | 1000 kcmil | Direct | 2 | 18 | 36 | 25 | 90 | 250 | Yes | 1 | 453.3 |  |  |  | 430.6 | Two circuits, 18 in c/c, direct buried
MV15-12 | 15 | 13.8 | 500 kcmil | Conduit | 2 | 12 | 36 | 25 | 90 | 250 | Yes | 1 | 281 |  |  |  | 266.9 | Two circuits, 12 in c/c, in conduit
MV15-13 | 15 | 13.8 | 500 kcmil | Direct | 1 | 48 | 36 | 25 | 120 | 300 | Yes | 1 | 299.7 |  |  |  | 284.6 | High soil resistivity (120/300)
MV15-14 | 15 | 13.8 | 500 kcmil | Direct | 1 | 48 | 36 | 35 | 90 | 250 | Yes | 1 | 303.1 |  |  |  | 287.9 | Elevated soil temperature 35 C
MV15-15 | 15 | 13.8 | 500 kcmil | Direct | 1 | 48 | 60 | 25 | 90 | 250 | Yes | 0.75 | 379.4 |  |  |  | 360.4 | Deeper burial 60 in, LF 0.75
MV25-01 | 25 | 24 | 4/0 AWG | Direct | 1 | 48 | 36 | 25 | 90 | 250 | Yes | 1 | 209.2 |  |  |  | 198.7 | Base: direct-buried trefoil, single circuit
MV25-02 | 25 | 24 | 250 kcmil | Direct | 1 | 48 | 36 | 25 | 90 | 250 | Yes | 1 | 229.7 |  |  |  | 218.2 | Base: direct-buried trefoil, single circuit
MV25-03 | 25 | 24 | 350 kcmil | Direct | 1 | 48 | 36 | 25 | 90 | 250 | Yes | 1 | 275.2 |  |  |  | 261.4 | Base: direct-buried trefoil, single circuit
MV25-04 | 25 | 24 | 500 kcmil | Direct | 1 | 48 | 36 | 25 | 90 | 250 | Yes | 1 | 333.3 |  |  |  | 316.6 | Base: direct-buried trefoil, single circuit
MV25-05 | 25 | 24 | 750 kcmil | Direct | 1 | 48 | 36 | 25 | 90 | 250 | Yes | 1 | 414.9 |  |  |  | 394.1 | Base: direct-buried trefoil, single circuit
MV25-06 | 25 | 24 | 1000 kcmil | Direct | 1 | 48 | 36 | 25 | 90 | 250 | Yes | 1 | 489 |  |  |  | 464.5 | Base: direct-buried trefoil, single circuit
MV25-07 | 25 | 24 | 4/0 AWG | Conduit | 1 | 48 | 36 | 25 | 90 | 250 | Yes | 1 | 195.1 |  |  |  | 185.3 | In PVC-40 conduit, single circuit
MV25-08 | 25 | 24 | 500 kcmil | Conduit | 1 | 48 | 36 | 25 | 90 | 250 | Yes | 1 | 305.4 |  |  |  | 290.1 | In PVC-40 conduit, single circuit
MV25-09 | 25 | 24 | 1000 kcmil | Conduit | 1 | 48 | 36 | 25 | 90 | 250 | Yes | 1 | 485.8 |  |  |  | 461.5 | In PVC-40 conduit, single circuit
MV25-10 | 25 | 24 | 500 kcmil | Direct | 2 | 18 | 36 | 25 | 90 | 250 | Yes | 1 | 313.1 |  |  |  | 297.4 | Two circuits, 18 in c/c, direct buried
MV25-11 | 25 | 24 | 1000 kcmil | Direct | 2 | 18 | 36 | 25 | 90 | 250 | Yes | 1 | 456.8 |  |  |  | 433.9 | Two circuits, 18 in c/c, direct buried
MV25-12 | 25 | 24 | 500 kcmil | Conduit | 2 | 12 | 36 | 25 | 90 | 250 | Yes | 1 | 281.9 |  |  |  | 267.7 | Two circuits, 12 in c/c, in conduit
MV25-13 | 25 | 24 | 500 kcmil | Direct | 1 | 48 | 36 | 25 | 120 | 300 | Yes | 1 | 303.6 |  |  |  | 288.4 | High soil resistivity (120/300)
MV25-14 | 25 | 24 | 500 kcmil | Direct | 1 | 48 | 36 | 35 | 90 | 250 | Yes | 1 | 306.6 |  |  |  | 291.2 | Elevated soil temperature 35 C
MV25-15 | 25 | 24 | 500 kcmil | Direct | 1 | 48 | 60 | 25 | 90 | 250 | Yes | 0.75 | 382.4 |  |  |  | 363.3 | Deeper burial 60 in, LF 0.75
Scenarios: 30 (15 kV: 15, 25 kV: 15) · Acceptance: ¦Δ%¦ ≤ 5% · EMBR v1.2 | [5 empty] | PASS count: | 0 | FAIL count: | 0